## Slide 1: Grounding Recommendations for On Site Power Systems
Brian Pumphrey

## Slide 2: Course Objectives
Grounding Recommendations for On Site Power Systems:
This course focuses on equipment and system grounding. Learners will understand the purpose of grounding and schemes to detect ground faults. This will lead to better understanding the selection of transfer switches (3-Pole vs 4-Pole), resistance grounding and grounding of paralleled generator sets.
Participants will be able to:
Understand the meaning of System grounding and Equipment grounding
Define the requirements for proper ground fault sensing to help design and install ground fault systems that work correctly
Define when a 3 pole verses 4 pole transfer switch should be used to reduce ground current loops, and assure ground fault detection systems work correctly
Identify key factors of Paralleled systems that need to be considered so that ground fault detection systems will work properly

## Slide 3: Equipment Grounding vs System Grounding
Equipment grounding
  Establishes a conductive path between normally non-current carrying metal parts of equipment and between these parts and the grounding electrode
  Earth connected to: non-current carrying parts
  Protect personnel
System grounding
  Deliberate connection between a circuit conductor of a power source and ground (earth)
  Earth connected to: current carrying parts
  Protect equipment
Both are paths for ground fault current
Metal Enclosures
Grounding Electrode
Neutral
System Ground
Equipment Ground

## Slide 4: Equipment Grounding vs System Grounding
Equipment grounding
  Establishes a conductive path between normally non-current carrying metal parts of equipment and between these parts and the grounding electrode
  Earth connected to: non-current carrying parts
  Protect personnel
System grounding
  Deliberate connection between a circuit conductor of a power source and ground (earth)
  Earth connected to: current carrying parts
  Protect equipment
Both are paths for ground fault current
Metal Enclosures
Grounding Electrode
Neutral
System Ground
Equipment Ground

## Slide 5: Equipment Grounding
Equipment Grounding Conductor (EGC)
Electrically connects the normally non–current-carrying metal parts of the equipment together to the:
  System grounded conductor (neutral)
  Grounding electrode conductor (GEC)
Grounding Electrode Conductor (GEC)
Provides the main low impedance path for ground fault current to trip the overcurrent device
Grounding Electrode:
A conducting object with a direct connection to earth, such as building steel or a ground rod
4 Pole ATS
Generator Set
GEC
EGC
Grounding Electrode
  Earth connected to: non-current carrying parts
  Protect personnel

## Slide 6: Why Ground Equipment?
Safety
Minimizes hazards of touching live equipment
Minimizes voltages on equipment during fault conditions
Provide a path for fault current to return to the source

## Slide 7: Impediments to Effective Equipment Grounding
Painted surfaces, use star washers to penetrate surface
Corroded or damaged connections, wires, or cables
Loose connections
Use flexible cable across anti-vibration mounts
Auxiliary enclosures require equipment ground
Corrosion
Auxiliary Enclosure
Anti-Vibration Mounts

## Slide 8: System Grounding
IEEE Std 142-2007 (Green Book)
Recommended Practice for Grounding of Industrial and Commercial Power Systems
System grounding is the intentional connection of a phase or neutral conductor to earth for the purpose of:
Controlling the voltage with respect to earth within predictable limits
Providing for a flow of current that will allow detection of an unwanted connection between system conductors and earth
Control of voltage to earth as to limit the voltage stress on the conductor insulation
Control of voltage for the reduction of shock hazards
C
A
B
G
N
C
A
B
N
Full Ground Fault on Phase B
IEEE: Institute of Electrical and Electronics Engineers
G
VA-G = 277 V
VC-G = 277 V
VB-G = 277 V
VN-G = 0 V
VA-G = 480 V
VC-G = 480 V
VB-G = 0 V
VN-G = 277 V
  Earth connected to: current carrying parts
  Protect equipment

## Slide 9: System Grounding Types
Solid Grounded
An intentional conductive path connected between a circuit conductor and ground
Impedance Grounded
A resistance (or impedance) is deliberately connected between a circuit conductor and ground
Ungrounded
No intentional connection between any circuit conductor and ground

## Slide 10: System Grounding - Solidly Grounded
Direct electrical connection to ground, most common grounding method for low voltage generator sets as there is no impedance in the circuit
The most common configuration is the solidly-grounded wye as it supports single-phase (3 wire) to neutral loads
Enables ground fault detection and thus activation of ground fault protection equipment
Detection of a fault is easy and immediate, however a high level fault could potentially damage the equipment
National Electrical Code (NEC) Article 250
N
L1
L2
L3

## Slide 11: System Grounding – Resistance (Impedance)
Grounded through resistance
Commonly used with medium voltage generator sets to limit the level of ground fault current -> GF detection needed
Low Resistance Grounding (LRG)
    Fault current usually limited to 200-800 amps
    Easily detectable with conventional CT’s
    Sufficient to trip circuit breakers
High Resistance Grounding (HRG)
    Fault current usually limited to 1-10 amps
    Intended to limit fault current to a level that is low enough to run safely but high enough so that ground fault relays can detect the fault
    Typically used in critical facilities
N
L1
L2
L3
National Electrical Code (NEC) Article 250
CT: Current Transformer

## Slide 12: System Grounding - Ungrounded
Zigzag or wye-delta transformers may be used to obtain a neutral for ungrounded systems
Either solidly grounded or resistance grounded
High impedance to balanced normal phase currents
Low impedance to zero sequence (fault) currents
National Electrical Code (NEC) Article 250
L1
L2
L3

## Slide 13
System Grounding (3 Wire System)
3P ATS
GenSet
To Loads
SERVICE
ENTRANCE
GEC
GEC
Grounding Electrode System
EGC
TO
UTILITY
3-phase 3-wire System (Neutral Not Used)
4 wire systems pass the neutral through
Generator May Be Solidly-Grounded (Shown), Resistance Grounded, or Ungrounded.
EGC (Equipment Grounding Conductor), ties enclosures together
GEC (Grounding Electrode Conductor)

## Slide 14: Separately / Non-Separately Derived System (4 Wire System)
No direct electrical connection between sources (Neutrals are not connected)
Generator Neutral is solidly bonded to Ground - Jumper
Common Neutral for entire system
Neutral is connected to ground at the Service, Not at the generator set
Separately Derived System
Non-Separately Derived System
NEUTRAL

## Slide 15: Separately Derived System (4 Wire System)
No direct electrical connection between sources (Neutrals are not connected)
3 Phase, 4 Wire System
4 Pole Transfer Switch
Generator Neutral is solidly bonded to Ground - Jumper
4 Pole ATS
To Loads (3-phase, 4 wire with GND)
GEC
Generator Set
GEC
EGC
Utility Service Entrance
System Bonding Jumper
TO
UTILITY
EGC (Equipment Grounding Conductor)
GEC (Grounding Electrode Conductor)
NEUTRAL
3 Phases

## Slide 16: Separately Derived System (4 Wire System)
Neutral to Ground Bond on generator (Jumper)
NEC Definition
  “An electrical source, other than a service, having no direct connection(s) to circuit conductors of any other electrical source other than those established by grounding and bonding connections”
NEC Section 250.30(A)(1)
  Separately derived systems to have a system bonding jumper connected between the generator frame and the grounded circuit conductor (neutral)
Some manufacturers ship the generator with the neutral bonded, some don’t. Need to be specified by customer
Neutral
Ground
National Electrical Code (NEC) Article 250
Bonding Jumper

## Slide 17: Non-Separately Derived System (4 Wire System)
Common Neutral for entire system
3-phase, 4 wire system
3 Pole Transfer Switch
Neutral is connected to ground at the Service, Not at the generator set
3 Pole ATS
Generator Set
To Loads (3-phase/4W with GND)
Utility Service Entrance
NEUTRAL
TO
UTILITY
3 Phases

## Slide 18: Ground Fault Sensing, Protection and Indication
NEC 230.95
Ground Fault Protection (GFP) of equipment is required at the Service disconnect (utility breaker) for systems with:
  Solidly grounded wye electrical service
  More than 150 volts to ground (277/480 or 347/600VAC)
  Over current device rating of 1000A or more
NEC 700.6 (D)
Ground Fault Indication (GFI) is required at the Emergency source

## Slide 19: How Do We Sense Ground Fault ?
Residual
  Most common method for circuit breakers
  CT on each phase and neutral
  Vector sum of current through all CT’s must be 0 (< threshold)
  Incoming and outgoing current must equal (Kirchoff’s Law)
GFR: Ground Fault Relay
CT: Current Transformer
Source ground return
  Single CT in the neutral to ground bond
  Method used by most genset controls
Zero sequence
  Single CT around all three phases and neutral
  Same concept as residual method

## Slide 20: Ground Fault Sensing in LV Emergency Standby Systems
Most common method is to use GFP at the disconnect breaker
Two rules for proper GF sensing:
  Rule #1: There must be only one neutral to ground connection on any neutral bus at one time
  Rule #2: Bonding connection must be between the ground fault sensor and the source
These two rules drive the requirement that 4 pole transfer switches must be used when ground fault sensing is required or may be required in the future.
IEEE Std 446-1995 (Orange Book)
Recommended Practice for Emergency and Standby Power Systems for Industrial and Commercial Applications
7.9.1 “for most emergency and standby power systems with ground-fault systems, switching of the grounded circuit conductor by the transfer switch is the recommended practice.”
LV: Low Voltage
GFP: Ground Fault Protection
IEEE: Institute of Electrical and Electronics Engineers

## Slide 21: Sensing a Ground Fault
3 Pole ATS
Generator Set
To Loads (3-phase/4 wire with GND)
Service Entrance
  Rule #1: There must be only one neutral to ground connection on any neutral bus at one time
  Rule #2: Bonding connection must be between the ground fault sensor and the source
3 Phase, 4 Wire System
3 Pole Transfer Switch
Ground Fault
CT
Ground fault will be sensed

## Slide 22
Parallel path for ground fault current on the neutral
GFP does not sense all fault current paths
Solution: remove the bond on the generator set
43Pole ATS
Generator Set
To Loads (3-phase/4 wire with GND)
Service Entrance
Two Bonding Jumpers
  Rule #1: There must be only one neutral to ground connection on any neutral bus at one time
  Rule #2: Bonding connection must be between the ground fault sensor and the source
3 Phase, 4 Wire System
3 Pole Transfer Switch
Ground Fault
GFP: Ground Fault Protection

## Slide 23
Single Bonding Jumper
  Rule #1: There must be only one neutral to ground connection on any neutral bus at one time
  Rule #2: Bonding connection must be between the ground fault sensor and the source
3 Phase, 4 Wire System
3 Pole Transfer Switch
Removing the generator set neutral bond solves the problem in the previous slide
There is only one path for earth fault current to return to the source
ATS
Generator Set
To Loads (3-phase/4W with GND)
Ground Fault

## Slide 24
3 Pole ATS
Generator Set
To Loads (3-phase/4 wire with GND)
Service Entrance
This violates “Rule #2”
Ground fault returns on neutral
Possible nuisance trip during exercise
3-Pole ATS Connected to Emergency Side
  Rule #1: There must be only one neutral to ground connection on any neutral bus at one time
  Rule #2: Bonding connection must be between the ground fault sensor and the source
Solution: ground the neutral on the source side of sensor (use 4 Pole ATS)

## Slide 25
4 Pole ATS
Generator Set
Service Entrance
Fourth pole opens the path on neutral
Allows accurate GFP sensing on both sources
The neutral is grounded in only one place at a time
Ground fault sensor is downstream of the bonding connection
To Loads (3-phase/4 wire with GND)
Function of 4-Pole Transfer Switches
  Rule #1: There must be only one neutral to ground connection on any neutral bus at one time
  Rule #2: Bonding connection must be between the ground fault sensor and the source
GFP: Ground Fault Protection

## Slide 26
Generator Set
3P ATS
Unbalanced
Load
Service Entrance
2 levels of GFP and 2 or more 3-pole ATS
Neutral current may nuisance trip feeder GFP during normal conditions
3P ATS
Distribution Board
Multiple Automatic Transfer Switch Applications
GFP: Ground Fault Protection

## Slide 27: Grounding of Paralleled Generator Sets
4 wire systems typically have a single ground in the switchgear
Generators in 3 wire systems are typically separately grounded
Medium or high voltage generators are often resistance grounded

## Slide 28: Ground Fault Sensing with Paralleled Systems
Multiple sources and multiple grounds add complexity
Switching the neutral with 4 pole breakers or ATS is not always practical
Modified Differential Ground Fault Protection (MDGFP) is required in many complex systems
  Multiple grounds
  4 wire system with 3 pole breakers/ATS (not breaking the neutral)
  Utility paralleling
  Fault isolation is required in tie breaker applications
MDGFP Differentiates between circulating neutral current and fault current

## Slide 29: Ground Fault Sensing with Paralleled Systems
4-Pole Breaker

## Slide 30: Modified Differential Ground Fault Protection
Circulating neutral current does not result in current flowing through the trip units.
Differentiates between circulating neutral current and fault current
Fault current results in current flowing through the trip units.

## Slide 31: Gensets Supplying Load, Normal Neutral Current Flow

## Slide 32: Gensets Supplying Load, Fault Current Flow

## Slide 33: Grounding Case Study
Nine containerized generator sets on metal platform
Containers bonded to platform
Platform connected to underground ground ring
Each generator is grounded through an NGR located inside the container

## Slide 34: Grounding Case Study
Load Bank
… …
Underground Ground Ring
Gen 9
Metal Platform
Platform is the fault current return path
Gen 1

## Slide 35: Grounding Case Study
Load Bank
… …
Underground Ground Ring
Gen 9
Metal Platform
Ground ring is the fault current return path
Gen 1

## Slide 36: Grounding Case Study
System ground consists of neutral conductors, NGRs, and ground ring
  System ground is intended to carry current – don’t rely on metal structures
Equipment ground consists of containers, platform, cabinets, etc., and ground ring
  Ground ring is common to both equipment and system ground
Establish a low impedance path for fault current to return to the source
  Path should be through ground ring, not across platform, cabinet, railings
Minimize step and touch potential hazard
NGR: Neutral Ground Resistor

## Slide 37
All equipment that can be energized must be grounded
Ground fault current must have a defined low impedance path to return to the source
Remember the two big rules for ground fault sensing in emergency standby systems:
  There can be only one neutral-to-ground bond in the system
  Bonding connection must be between the ground fault sensor and the source
Paralleled sources may require complex ground fault schemes
  Modified Differential GFP can differentiate between fault current and normal neutral current in systems with multiple sources and grounds
  Multiple grounds, 4 wire solid neutral systems and utility paralleling applications may require MDGFP
Recommendations

## Slide 38: Course Summary
Grounding Recommendations for On Site Power Systems:
Understand the meaning of System grounding and Equipment grounding
Define the requirements for proper ground fault sensing to help design and install ground fault systems that work correctly
Define when a 3 pole verses 4 pole transfer switch should be used to reduce ground current loops, and assure ground fault detection systems work correctly
Identify key factors of Paralleled systems that need to be considered so that ground fault detection systems will work properly
Specify
Specify 4 Pole ATS if:
  GF Protection on Normal Service / GF Indication on Emergency is required
  Any 3 phase 4-wire with line-to-ground voltage above 150V when future expansion to the facility is expected

## Slide 39
Q+A